## Sheet1
[7 empty] | Generator |  |  |  | Generator |  |  |  | Mains Power Cabinet |  |  |  |  | Additional Power cabinet |  |  |  |  | Batteries |  |  |  | Aircon 1 |  |  | Aircon 2 |  |  | SOLAR |  |  |  | Environnement Statut |  |  |  | SHELTER
Site ID IHS | ID Operator | Name site | Topology | Indoor/Outdoor | SBC | # nber of Gen | Brand | Engine brand | Alternator brand | Capacity (KVA) | Brand | Engine brand | Alternator brand | Capacity (KVA) | Brand | Capacity (KW) | Rectifier Module type | Module Size (KW) | Rectifier Number | Brand | Capacity (KW) | Rectifier Module type | Module Size (KW) | Rectifier Number | Brand | Capacity (V/AH) | Battery type | Battery Number | Brand | Capacity (V/W) | Statut (OK/NOK) | Brand | Capacity (V/W) | Statut (OK/NOK) | #Nber of pannel | Brand | Capacity | Working (OK/NOK) | Leakage OK/NOK | Abandonned equipment on site YES/NO | Site cleaning OK/NOK | Light Statut OK/NOK | Shelter statut | Comments if we have issues on site | Timeline to closed those issues | Overall site statut SBC Feedback | Final Site statut SS OK/NOK | DATE | j | j | j | j | j
IHS_EDA_015 | LIT_314 | Edea-Nkakanzock | Grid-Gen | Outdoor | GRATO | 1 | EARTH TECHNOLOGIY |  |  | 15 | [5 empty] | IPT - 12 KW | DELTA |  | 2 | [6 empty] | No name | No name | 16 | [15 empty] | ;POOR BACKUP; |  |  |  | 2026-02-19 15:00
IHS_DLA_290 | LIT_297 | Lendi-Entree | Grid-Gen | Outdoor | GRATO | 0 | TRION |  |  | 30 | [5 empty] | ZTE 36 KW | ZTE |  | 8 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 8 | [15 empty] | ;GRILLE DE PROTECTION NON SOUDEE; |  |  |  | 2026-02-19 15:00
IHS_EDA_007 | T1772 | Edea Beon | Grid-Gen | Outdoor | GRATO | 0 | TRION |  |  | 20 | [5 empty] | IPT - 12 KW | DELTA |  | 2 | [6 empty] | Monbat 170 AH | Monbat 170 AH | 8 | [15 empty] | ALTERNATEUR DE CHARGE FAULTY; CHARGEUR STATISQUE FAULTY;1/2 REDRESSEUR FAULTY/ LE pcs3 n'affiche pas la valeur du load; |  |  |  | 2026-02-19 15:00
IHS_DLA_223 | LIT_106 | Denver | Grid-Gen | Indoor | GRATO | 1 | COLOR CERAMICA |  |  | 15 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | Sacred sun 12V-175AH | Sacred sun 12V-175AH | 8 | [19 empty] | 2026-02-19 15:00
IHS_EDA_016 | LIT_323 | Okoth | Grid-Gen | Outdoor | GRATO | 1 | G POWER |  |  | 15 | [5 empty] | IPT 24 KW | DELTA |  | 3 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 4 | [15 empty] | ;LE PSC3 N'AFFICHE PAS LE LOAD / CONTACTEUR ET DISJONCTEUR ENEO FAULTY/ RCP FAULTY; |  |  |  | 2026-02-19 15:00
IHS_DLA_432 | LIT_446 | Bonamoussadi Hôpital | Grid-Gen | Outdoor | GRATO | 1 | IPT TRION |  |  | 15 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 16 | [15 empty] | ;2 RACK DE BATTERIE FONCTIONNELLE SUR 4; |  |  |  | 2026-02-19 15:00
IHS_DLA_450 | LIT_454 | Kotto Eglise EPC | Grid-Gen | Outdoor | GRATO | 1 | GB POWER |  |  | 15 | [5 empty] | ZTE 24 KW | ZTE |  | 6 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 4 | [19 empty] | 2026-02-19 15:00
IHS_DLA_227 | T0864 | Bonamoussadi Careffour | Grid-Gen | Outdoor | GRATO | 1 | Jubaili Bros |  |  | 17 | [5 empty] | IPT - 12KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 16 | [19 empty] | 2026-02-19 15:00
IHS_DLA_225 | T2295 | New Bonamoussadi | Grid-Gen | Outdoor | GRATO | 1 | ELCOS |  |  | 17 | [5 empty] | IPT - 12KW | DELTA |  | 4 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 16 | [19 empty] | 2026-02-19 15:00
IHS_DLA_485 | T2759 | Denver Total | Grid-Gen | Outdoor | GRATO | 1 | JUBALI BROSS |  |  | 30 | [5 empty] | IPT - 12 KW | DELTA |  | 4 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [15 empty] | LE GE NE SUPPORTE PLUS LA CHARGE/ AFFICHEUR DE LA CARTE FAULTY;PL7 3 N'AFFICHE PLUS LES VALEURS/ POOR BACKUP; |  |  |  | 2026-02-19 15:00
IHS_DLA_423 | T1732 | Bonaberi Isenbeck | Grid-Gen | Outdoor | GRATO | 1 | GMC |  |  | 33 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 8 | [6 empty] | CD TRUE 12V-172AH | CD TRUE 12V-172AH | 24 | [19 empty] | 2026-01-26 09:00
IHS_BNB_100 | T1940 | ngwelle 2 | Grid-Gen | Outdoor | GRATO | 1 | TECHNO |  |  | 20 | [5 empty] | IPT 12 KW | DELTA |  | 5 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-01-28 19:00
IHS_BNB_103 | LIT_621 | Minkwele2 | Grid-Gen | Outdoor | GRATO | 1 | GB POWER |  |  | 33 | [5 empty] | ZTE 36 KW | ZTE |  | 9 | [6 empty] | VISION 48V-150AH | VISION 48V-150AH | 5 | [15 empty] | COMPTEUR MECANIQUE INSTALLE;CLIM DE LA BAIE FAULTY/LE PSC3 N'AFFICHE PAS/PARAFOUDRE DE TYPE 2 FAULTY; |  |  |  | 2026-01-26 07:30
IHS_DLA_456 | LIT_456 | Edea Mbondanjick | Gen-Lithium | Outdoor | GRATO | 1 | TECNO-GEN |  |  | 20 | [5 empty] | HUAWEI-24KW | HUAWEI |  | 6 | [6 empty] | Lithium 100AH | Lithium 100AH | 2 | [19 empty] | 2026-01-26 10:17
IHS_EDA_070 | LIT_519 | Mandjap | Hybrid-Gen | Outdoor | GRATO | 1 | GB POWER |  |  | 17 | [5 empty] | IPT - 12 KW | DELTA |  | 2 | [6 empty] | power cycle - 165 AH | power cycle - 165 AH | 12 | [19 empty] | 2026-01-27 09:00
IHS_EDA_064 | LIT_506 | Sokelle | Gen Only | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-26 05:00
IHS_BNB_102 | LIT_622 | Ndobo3 | Grid-Gen | Outdoor | GRATO | 1 | GB POWER |  |  | 33 | [5 empty] | IPT 12 KW | CLIM FAULTY |  | 5 | [6 empty] | Ritar 12V-180AH | Ritar 12V-180AH | 16 | [19 empty] | 2026-01-27 17:00
IHS_DLA_433 | LIT_442 | Cite de Paix | Grid-Gen | Outdoor | GRATO | 1 | MIKANO |  |  | 15 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [15 empty] | ;2 EXTRACTEURS D'AIR FAULTY/LA BAIE NE SE FERME PAS; |  |  |  | 2026-01-28 07:00
IHS_BNB_104 | LIT_017 | Bberi-Chateau | Grid-Gen | Indoor | GRATO | 0 | JMG |  |  | 33 | [5 empty] | ZTE 24 KW | ZTE |  | 6 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 6 | [19 empty] | 2026-01-27 18:00
IHS_EDA_030 | LIT_231 | Nkak | Solar-Gen-Lithium | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | Huawei - 24 KW | HUAWEI |  | 5 | [6 empty] | Lithium 48V-150AH | Lithium 48V-150AH | 2 | [15 empty] | ;2/8 redresseurs faulty; |  |  |  | 2026-01-26 19:00
IHS_EDA_066 | LIT_510 | Kanga | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 13 | [5 empty] | IPT 12KW | DELTA |  | 2 | [6 empty] | Vision 12V-180AH | Vision 12V-180AH | 16 | [19 empty] | 2026-01-26 15:00
IHS_DLA_138 | LIT_098 | Cite-Sic | Grid-Gen | Indoor | GRATO | 1 | MIKANO |  |  | 30 | [5 empty] | IPT 12 KW | DELTA |  | 2 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [19 empty] | 2026-01-26 10:00
IHS_BNB_028 | LIT_346 | Bberi-Abattoir | Grid-Gen | Outdoor | GRATO | 0 | GB POWER |  |  | 30 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 5 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [19 empty] | 2026-01-26 15:00
IHS_EDA_024 | LIT_388 | Sikoum-II | Gen-Lithium | Outdoor | GRATO | 1 | IPT TRION |  |  | 15 | [5 empty] | HUAWEI 24KW | HUAWI |  | 6 | [6 empty] | Lithium 100AH | Lithium 100AH | 2 | [19 empty] | 2026-01-26 14:00
IHS_BNB_017 | LIT_094 | Mabanda | Grid-Gen | Outdoor | GRATO | 1 | JMG |  |  | 30 | [5 empty] | ZTE 36 KW | ZTE |  | 9 | [6 empty] | ZTE 54V/100AH | ZTE 54V/100AH | 4 | [19 empty] | 2026-01-27 16:40
IHS_EDA_031 | LIT_006 | Ferme-Suisse | Grid-Gen | Indoor | GRATO | 1 | MIKANO |  |  | 20 | [5 empty] | ZTE 36 KW | ZTE |  | 7 | [6 empty] | VISION 48V/125AH | VISION 48V/125AH | 4 | [15 empty] | ;PSC3 FAULTY; |  |  |  | 2026-01-26 12:50
IHS_BNB_032 | LIT_203 | Bonamatoumbe | Grid-Gen | Indoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 8 | [15 empty] | AC FAULTY, SHELTER OPEN |  |  |  | 2026-01-30 23:08
IHS_BNB_021 | LIT_260 | Ndobo-Rail | Grid-Gen | Outdoor | GRATO | 1 | GB POWER |  |  | 30 | [5 empty] | IPT 24 KW | DELTA |  | 5 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-01-28 07:00
IHS_BNB_006 | LIT_243 | Bberi-Centre | Grid-Gen | Outdoor | GRATO | 1 | GMG |  |  | 33 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 6 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [19 empty] | 2026-01-26 17:00
IHS_DLA_443 | LIT_435 | Bonassama IHS | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | ZTE 36 KW | ZTE |  | 6 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 5 | [19 empty] | 2026-02-05 09:40
IHS_BNB_004 | LIT_291 | Grand-Hangar | Grid-Gen | Outdoor | GRATO | 1 | IPT TRION |  |  | 30 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | NO NAME | NO NAME | 12 | [19 empty] | 2026-01-26 21:46
IHS_DLA_402 | LIT_151 | Base-elf-new | Grid-Gen | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 20 | [5 empty] | HUAWEI 24 KW | HUAWEI |  | 8 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 16 | [19 empty] | 2026-02-07 15:50
IHS_EDA_014 | LIT_229 | Edea-Entree | Solar-Grid-Gen | Outdoor | GRATO | 1 | JUBALIS BRO |  |  | 20 | [5 empty] | DYNAMIQUE POWER | DYNAMIQUE POWER |  | 6 | [6 empty] | 48V/150AH | 48V/150AH | 4 | [15 empty] | CHARGEUR STATISQUE, BATTERY GE, FAULTY;RCP FAULTY; |  |  |  | 2026-01-30 14:00
IHS_EDA_042 | SUO_029 | Ngambe | Grid-Gen-Lithium | Indoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-30 10:00
IHS_DLA_257 | LIT_303 | Kotto-Antenne | Grid-Gen | Outdoor | GRATO | 1 | GB POWER |  |  | 30 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 8 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-01-28 12:15
IHS_DLA_298 | LIT_012 | Sikoum | Solar-Gen-Lithium | Indoor | GRATO | 1 | IPT TRION |  |  | 22 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 6 | [6 empty] | Lithium 100AH | Lithium 100AH | 3 | [19 empty] | 2026-01-26 16:00
IHS_EDA_020 | CTR_059 | Ndokok | Grid-Gen | Indoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT - 12 KW | DELTA |  | 2 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-01-26 17:45
IHS_KRI_016 | SUD_004 | Pama | Grid-Gen | Indoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 8 | [15 empty] | TUYAU D'ECHAPPEMENT COUPE |  |  |  | 2026-02-04 16:00
IHS_DLA_164 | LIT_083 | ZI-Bassa | Grid-Gen | Indoor | GRATO | 1 | MAHINDRA |  |  | 30 | [5 empty] | IPT 24 KW | DELTA |  | 5 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [19 empty] | 2026-01-27 11:00
IHS_EDA_005 | LIT_078 | Edea-Ville | Grid-Gen | Indoor | GRATO | 1 | Tecno Gen |  |  | 20 | [5 empty] | ZTE 36 KW | ZTE |  | 6 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 4 | [15 empty] | CHARGEUR STATIQUE FAULTY |  |  |  | 2026-02-19 08:00
IHS_EDA_017 | LIT_230 | Edea-Ndokok | Grid-Gen | Outdoor | GRATO | 1 | SACCAL |  |  | 15 | [5 empty] | IPT - 12 KW | DELTA |  | 3 | [6 empty] | RITAR 12V-170AH | RITAR 12V-170AH | 4 | [19 empty] | 2026-01-26 17:00
IHS_EDA_037 | LIT_308 | Ndokoma | Grid-Gen-Lithium | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 20 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 6 | [6 empty] | LITHUIM 12V-170AH | LITHUIM 12V-170AH | 3 | [19 empty] | 2026-02-09 16:00
IHS_DLA_293 | LIT_306 | Missole-Entree | Solar-Gen-Lithium | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 20 | [5 empty] | Huawei - 24 KW | HUAWEI |  | 6 | [6 empty] | HAUWEI 48V/1000AH | HAUWEI 48V/1000AH | 2 | [15 empty] | FUITE D'HUILE AU NIVEAU DU JOINT DU CARTER/POMPE A INJECTION FAULTY |  |  |  | 2026-01-26 18:00
IHS_DLA_493 | LIT_093 | Ndogpassi Nodal | Off Air | Off Air | GRATO | 1 | Staunch Machinery |  |  | 15 | [5 empty] | IPT - 12 KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-170AH | MONBAT 12V-170AH | 16 | [15 empty] | ;POOR BACKUP; |  |  |  | 2026-01-29 07:00
IHS_EDA_013 | LIT_321 | Edea-Lom | Grid-Gen | Outdoor | GRATO | 1 | Earth Technologies |  |  | 22 | [5 empty] | IPT - 12 KW | DELTA |  | 3 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 3 | [19 empty] | 2026-01-28 11:19
IHS_EDA_012 | LIT_322 | Edea-Ekite | Grid-Gen | Outdoor | GRATO | 1 | HABBIB |  |  | 12.5 | [5 empty] | ZTE 36 KW | ZTE |  | 6 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 4 | [15 empty] | CHARGEUR STATISQUE ET BATTERY GE FAULTY;PARAFOUDRE FAULTY; |  |  |  | 2026-02-02 12:00
IHS_DLA_273 | LIT_358 | Bonangang | Grid-Gen | Outdoor | GRATO | 1 | SACCAL |  |  | 33 | [5 empty] | IPT 24 KW | DELTA |  | 7 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [19 empty] | 2026-01-26 15:30
IHS_BNB_029 | LIT_361 | Grand-Hangar-II | Grid-Gen | Outdoor | GRATO | 1 | GB POWER |  |  | 30 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | NO NAME | NO NAME | 16 | [19 empty] | 2026-01-28 08:00
IHS_DLA_296 | LIT_227 | Missole | Hybrid-Gen | Outdoor | GRATO | 1 | TECNO GEN |  |  | 20 | [5 empty] | HUAWEI -12-KW | HUAWEI |  | 5 | [6 empty] | HUAWEI 48V/100AH | HUAWEI 48V/100AH | 2 | [19 empty] | 2026-01-26 21:00
IHS_EDA_004 | LIT_313 | Edea-Bisseke | Grid-Gen | Outdoor | GRATO | 1 | MIKANO |  |  | 20 | [5 empty] | IPT - 24 KW | DELTA |  | 5 | [6 empty] | AGIsson 12V-170 AH | AGIsson 12V-170 AH | 24 | [15 empty] | AFFICHEUR FLOUE DE LA CARTE;PARAFOUDRE FAULTY; |  |  |  | 2026-01-28 09:00
IHS_EDA_067 | LIT_512 | Apouh | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT - 12 KW | DELTA |  | 2 | [6 empty] | POWER CYCLE | POWER CYCLE | 16 | [15 empty] | PSC3 N'affiche pas la valeur du load;PSC3 FAULTY; |  |  |  | 2026-02-02 15:30
IHS_EDA_069 | LIT_515 | Sodibanga | Hybrid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT - 12 KW | DELTA |  | 3 | [6 empty] | HUAWEI 48V/150AH | HUAWEI 48V/150AH | 4 | [19 empty] | 2026-01-27 11:13
IHS_DLA_272 | LIT_246 | Kotto-Bloc | Grid-Gen | Outdoor | GRATO | 1 | JET GENERATOR |  |  | 30 | [5 empty] | IPT 24 KW | DELTA |  | 6 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 16 | [19 empty] | 2026-01-26 10:30
IHS_BNB_022 | LIT_377 | Ngwelle-II | Grid-Gen | Outdoor | GRATO | 1 | GB POWER |  |  | 33 | [5 empty] | IPT 12KW | DELTA |  | 4 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-01-27 13:00
IHS_DLA_228 | LIT_357 | Makepe-AES | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT - 12KW | DELTA |  | 4 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 16 | [19 empty] | 2026-01-27 11:00
IHS_BNB_009 | LIT_290 | Bonabappe | Grid-Gen-Lithium | Outdoor | GRATO | 1 | SACCAL |  |  | 30 | [5 empty] | IPT 12 KW | DELTA |  | 4 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [19 empty] | 2026-01-26 22:58
IHS_DLA_190 | LIT_373 | Missoke-Universite | Grid-Gen | Outdoor | GRATO | 1 | SDMO |  |  | 45 | [5 empty] | HUAWEI 24KW | HUAWEI R4850G |  | 6 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 8 | [19 empty] | 2026-01-26 12:00
IHS_DLA_255 | LIT_247 | Bsadi-BlocJ | Grid-Gen | Outdoor | GRATO | 1 | TECHNO-GEN |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 5 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 16 | [19 empty] | 2026-01-28 09:30
IHS_DLA_127 | LIT_263 | CCC | Grid-Gen-Lithium | Outdoor | GRATO | 1 | MAHINDRA |  |  | 30 | [5 empty] | IPT 12 KW | DELTA |  | 5 | [6 empty] | SHL 12V/180AH | SHL 12V/180AH | 16 | [15 empty] | ;8/16 BATTERIES BACKUP FAULTY ET DECONNECTE/CLIM FAULTY/2 EXTRACTEURS FAULTY; |  |  |  | 2026-01-27 07:00
IHS_DLA_199 | LIT_342 | Logbaba-SONEL | Grid-Gen-Lithium | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 20 | [5 empty] | HUAWEI 24 KW | HUAWEI |  | 6 | [6 empty] | 0 | 0 | 6 | [19 empty] | 2026-01-29 08:00
IHS_EDA_032 | LIT_108 | Ngwei | Solar-Grid-Gen | Indoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [15 empty] | ;LA CLIM FAULTY/ 3 EXTRACTEURS FAULTY/ PAS DE PARAFOUDRE; |  |  |  | 2026-01-30 11:00
IHS_YND_701 | LIT_514 | NKAN | Gen-Lithium | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-26 14:00
IHS_EDA_114 | LIT_201 | Pouma Makop | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 2 | [6 empty] | Monbat 12V-180AH | Monbat 12V-180AH | 16 | [19 empty] | 2026-01-28 17:00
IHS_EDA_101 | LIT_121 | NGOG MBOG | Gen-Lithium | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-26 18:00
IHS_EDA_043 | LIT_319 | Botko | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-28 15:00
IHS_BNB_008 | LIT_206 | Ngwele | Grid-Gen | Indoor | GRATO | 1 | TECNO-GEN |  |  | 20 | [5 empty] | ZTE 36 KW | ZTE |  | 6 | [6 empty] | ZTE 48V/150AH | ZTE 48V/150AH | 3 | [19 empty] | 2026-01-27 08:00
IHS_BNB_023 | LIT_364 | Bonamatoumbe-II | Grid-Gen | Outdoor | GRATO | 0 | TECHNO GEN |  |  | 12.5 | [5 empty] | IPT 12KW | DELTA |  | 2 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-01-27 13:42
IHS_BNB_036 | T1698 | Minkwele | Grid-Gen | Outdoor | GRATO | 1 | MIKANO |  |  | 33 | [5 empty] | IPT 12 KW | DELTA |  | 4 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-01-27 09:00
IHS_DLA_468 | T1359 | MABANDA 3 | Grid-Gen | Outdoor | GRATO | 1 | IPT TRION |  |  | 20 | [5 empty] | PDC 64 KW | PDC |  | 4 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 4 | [19 empty] | 2026-01-26 16:00
IHS_BNB_026 | T0016 | Bonaberi Warehouse | Grid-Gen | Indoor | GRATO | 1 | Earth Technologies |  |  | 45 | [5 empty] | IPT 24 KW | DELTA |  | 6 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 32 | [19 empty] | 2026-01-27 09:30
IHS_BNB_012 | T0452 | Sodiko Gare Routiere | Grid-Gen | Outdoor | GRATO | 1 | MAHINDRA |  |  | 30 | [5 empty] | ZTE 36 KW | ZTZ |  | 9 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 6 | [19 empty] | 2026-01-27 15:30
IHS_BNB_101 | T1935 | Ndobo | Grid-Gen | Indoor | GRATO | 1 | ELCOS |  |  | 30 | [5 empty] | IPT 24 KW | DELTA |  | 6 | [6 empty] | 0 | 0 | 0 | [15 empty] | CARTE GE ILLISIBLE;PSC3 FAULTY; |  |  |  | 2026-01-27 09:00
IHS_BNB_105 | T2511 | Bonaberi matelot | Grid-Gen-Lithium | Outdoor | GRATO | 1 | SUPERNOVA |  |  | 30 | [5 empty] | FNS POWER 36 KW | FNS |  | 12 | [6 empty] | VISION 48V-150AH | VISION 48V-150AH | 4 | [19 empty] | 2026-01-28 17:00
IHS_BNB_111 | T2613 | Bepelle bloc | Grid-Gen-Lithium | Outdoor | GRATO | 1 | GB POWER |  |  | 15 | [5 empty] | FNS POWER 24 KW | FNS |  | 8 | [6 empty] | LITHUIM 48V-100AH | LITHUIM 48V-100AH | 1 | [19 empty] | 2026-01-27 16:30
IHS_BNB_110 | T2094 | Bonaminkano Dikolo | Grid-Gen-Lithium | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 15 | [5 empty] | FNS POWER 36 KW | FNS |  | 3 | [6 empty] | LITHUIM 48V-100AH | LITHUIM 48V-100AH | 1 | [15 empty] | ;CONTROLLEUR MISSING; |  |  |  | 2026-01-26 14:03
IHS_YND_417 | T0298 | Sombo | Grid-Gen | Indoor | GRATO | 2 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [15 empty] | ;3 EXTRACTEURS FAULTY/ VENTILLATEUR EVAPORATEUR FAULTY.; |  |  |  | 2026-02-04 08:00
IHS_BNB_011 | T1701 | FORET BAR MABANDA | Grid-Gen | Outdoor | GRATO | 1 | SACCAL |  |  | 20 | [5 empty] | IPT 24 KW | DELTA |  | 5 | [6 empty] | CD TRUE 12C-175AH | CD TRUE 12C-175AH | 32 | [19 empty] | 2026-01-26 22:07
IHS_BNB_005 | T0867 | BONABERI MICHELIN 867 | Grid-Gen | Indoor | GRATO | 1 | MIKANO |  |  | 30 | [5 empty] | ZTE 36 KW | ZTE |  | 9 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 7 | [19 empty] | 2026-01-26 21:30
IHS_BNB_030 | T0275 | Mabanda | Grid-Gen | Indoor | GRATO | 1 | MIKANO |  |  | 45 | [5 empty] | ZTE 36 KW | ZTE |  | 9 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 5 | [19 empty] | 2026-01-26 12:39
IHS_DLA_404 | T1390 | Bonaberi Magzi | Grid-Gen | Outdoor | GRATO | 1 | MIKANO |  |  | 30 | [5 empty] | ZTE 36 KW | ZTE |  | 9 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 6 | [19 empty] | 2026-01-26 19:22
IHS_DLA_404 | T1390 | Bonaberi Magzi | Grid-Gen | Outdoor | GRATO | 1 | MIKANO |  |  | 30 | [5 empty] | ZTE 36 KW | ZTE |  | 9 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 6 | [19 empty] | 2026-01-26 19:22
IHS_DLA_448 | LIT_444 | Bonaberi Q des Prince | Grid-Gen | Outdoor | GRATO | 1 | MAHINDRA |  |  | 15 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 4 | [19 empty] | 2026-01-27 13:44
IHS_BNB_018 | T0518 | Bonamatoumbe | Grid-Gen | Outdoor | GRATO | 1 | MAHINDRA |  |  | 20 | [5 empty] | ZTE 36KW | ZTE |  | 6 | [6 empty] | VISION 48/150 | VISION 48/150 | 6 | [19 empty] | 2026-02-02 10:00
IHS_BNB_035 | T0620 | Bodjongo | Grid-Gen | Outdoor | GRATO | 1 | GB POWER |  |  | 30 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 6 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 3 | [15 empty] | ;POOR BACKUP; |  |  |  | 2026-01-26 20:30
IHS_BNB_016 | LIT_046 | Du-Levant | Grid-Gen | Indoor | GRATO | 1 | MIKANO |  |  | 13 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 8 | [19 empty] | 2026-01-26 13:43
IHS_BNB_020 | T1797 | Sodiko 2 | Grid-Gen | Outdoor | GRATO | 1 | MIKANO |  |  | 20 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-01-30 20:30
IHS_YND_700 | LIT_507 | Sibongo | Grid-Gen | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 9 | [5 empty] | IPT 12 KW | DELTA |  | 2 | [6 empty] | MONBAT 12V-172AH | MONBAT 12V-172AH | 16 | [15 empty] | ;PARAFOUDRE FAULTY; |  |  |  | 2026-01-29 17:00
IHS_BNB_007 | T0597 | Ngwelle | Grid-Gen | Outdoor | GRATO | 1 | TECHNO-GEN |  |  | 20 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-01-27 07:30
IHS_BNB_107 | T3235 | Bonaberi 4 Etages | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 9 | [5 empty] | VISION 24 KW | HUAWEI |  | 3 | [6 empty] | SACRED-SUN 12V-170AH | SACRED-SUN 12V-170AH | 16 | [19 empty] | 2026-01-27 21:38
IHS_BNB_108 | T3218 | Ndobo Excellence | Grid-Gen | Outdoor | GRATO | 1 | MAHINDRA |  |  | 20 | [5 empty] | VISION 24 KW | HUAWEI |  | 5 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-01-27 21:01
IHS_EDA_026 | T1734 | Logbadjeck | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT - 12 KW | DELTA |  | 3 | [6 empty] | RITAR 12V-175AH | RITAR 12V-175AH | 16 | [15 empty] | BATTERY FAULTY;Fuite d'huile au niveau du carter inférieur et supérieur; |  |  |  | 2026-01-26 13:42
IHS_BNB_109 | T2506 | BODJONGO ABEDI | Grid-Gen-Lithium | Outdoor | GRATO | 1 | GB POWER |  |  | 15 | [5 empty] | FNS POWER 24 KW | FNS |  | 8 | [6 empty] | LITHUIM 48V-100AH | LITHUIM 48V-100AH | 1 | [19 empty] | 2026-01-27 21:30
IHS_DLA_534 | T2085 | LENDI RUE DUPLEX | Grid-Gen | Outdoor | GRATO | 1 | SUPERNOVA |  |  | 30 | [5 empty] | ZTE 36 KW | ZTE |  | 9 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 4 | [19 empty] | 2026-01-29 12:30
IHS_EDA_061 | T2550 | EDEA BISSEKE MARKET | Gen Only | Outdoor | GRATO | 1 | IPT POWER TECH |  |  | 15 | [5 empty] | IPT 12 KW | DELTA |  | 1 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 2 | [15 empty] | ;ALTERNATEUR DE CHARGE FAULTY; |  |  |  | 2026-01-28 10:00
IHS_DLA_163 | LIT_024 | Socaver | Grid-Gen | Indoor | GRATO | 1 | YOUNESS |  |  | 13 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 8 | [19 empty] | 2026-01-27 16:00
IHS_DLA_254 | LIT_057 | Bsadi-Terminus | Grid-Gen-Lithium | Indoor | GRATO | #N/A | #N/A |  |  | #N/A | [5 empty] | #N/A | #N/A |  | #N/A | [6 empty] | #N/A | #N/A | #N/A | [19 empty] | #N/A
IHS_EDA_036 | LIT_069 | Pouma | Grid-Gen | Indoor | GRATO | 1 | TECHNO GEN |  |  | 15 | [5 empty] | IPT 12 KW | DELTA |  | 2 | [6 empty] | MONBAT 12V-180AH | MONBAT 12V-180AH | 16 | [19 empty] | 2026-02-05 11:00
IHS_EDA_022 | LIT_113 | Dizangue | Grid-Gen | Indoor | GRATO | 1 | TECHNO-GEN |  |  | 12.5 | [5 empty] | IPT 12KW | DELTA |  | 2 | [6 empty] | no name | no name | 16 | [15 empty] | FUITE D'HUILE AU NIVEAU DU CARTER INFERIEUR;PARAFOUDRE FAULTY/ CONTROLLEUR N'AFFICHE PAS LA VALEUR DU LOAD; |  |  |  | 2026-01-26 09:00
IHS_EDA_040 | LIT_135 | Ngonga | Grid-Gen | Indoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V/180AH | MONBAT 12V/180AH | 16 | [19 empty] | 2026-02-02 17:00
IHS_EDA_044 | LIT_138 | Sackbayeme | Grid-Gen | Indoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-29 11:00
IHS_BNB_033 | LIT_181 | Bonendale | Grid-Gen | Indoor | GRATO | 1 | MAHINDRA |  |  | 20 | [5 empty] | ZTE 36 KW | ZTE |  | 6 | [6 empty] | SACRES SUN 48V/175AH | SACRES SUN 48V/175AH | 8 | [19 empty] | 2026-01-30 10:00
IHS_EDA_039 | LIT_191 | Mouanko | Grid-Gen | Indoor | GRATO | 1 | IPT TRION |  |  | 20 | [5 empty] | IPT - 12 KW | DELTA |  | 2 | [6 empty] | RITAR 12V-180AH | RITAR 12V-180AH | 8 | [19 empty] | 2026-01-27 16:00
IHS_DLA_126 | LIT_217 | Ndokoti-New | Grid-Gen | Outdoor | GRATO | 1 | MAHINDRA |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 4 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [15 empty] | ;EXTRACTEURS FAULTY; |  |  |  | 2026-01-30 10:00
IHS_DLA_216 | LIT_224 | Makepe-St-Tropez | Grid-Gen | Outdoor | GRATO | 1 | Tecno Gen |  |  | 20 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 8 | [6 empty] | RITAR 12V-180AH | RITAR 12V-180AH | 12 | [19 empty] | 2026-01-28 12:00
IHS_DLA_187 | LIT_267 | Sable | Grid-Gen | Outdoor | GRATO | 1 | EARTH TECHNOLOGIE |  |  | 22 | [5 empty] | IPT 12KW | DELTA |  | 5 | [6 empty] | Sacred sun 12V/175AH | Sacred sun 12V/175AH | 16 | [15 empty] | ;LE POWER CABINET IPT NE SE FERME PAS HERMETIQUEMENT SON SYSTÈME DE FERMETURE HS; |  |  |  | 2026-01-26 16:40
IHS_BNB_031 | LIT_362 | Bonabappe-II | Grid-Gen | Outdoor | GRATO | 1 | MAHINGRA |  |  | 15 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | SACRED SUN 48V-175AH | SACRED SUN 48V-175AH | 8 | [15 empty] | ; CLIM FAULTY; |  |  |  | 2026-01-27 14:21
IHS_DLA_229 | LIT_400 | Bonawon | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | ELTEK 8KW | FLATPACK |  | 3 | [6 empty] | sacred sun 12V/175AH | sacred sun 12V/175AH | 8 | [19 empty] | 2026-01-28 17:20
IHS_DLA_156 | LIT_401 | Makepe-Maturite | Grid-Gen | Outdoor | GRATO | 1 | FG WILSON |  |  | 15 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 16 | [19 empty] | 2026-01-26 07:00
IHS_DLA_452 | LIT_450 | Quartier Gentil | Grid-Gen | Outdoor | GRATO | 1 | TECNO-GEN |  |  | 15 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | 12HRV 170AH | 12HRV 170AH | 16 | [15 empty] | GEN OVER LOAD;1 EXTRACTEUR D'AIR ET PARAFOUDRE FAULTY;1 EXTRACTEUR D'AIR ET PARAFOUDRE FAULTY |  |  |  | 2026-01-29 10:00
IHS_EDA_060 | LIT_508 | Logbong | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-29 13:00
IHS_EDA_065 | LIT_509 | Kopongo | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT- 12 KW | DELTA |  | 2 | [6 empty] | RITAR 12V-175AH | RITAR 12V-175AH | 2 | [19 empty] | 2026-01-30 14:00
IHS_EDA_068 | LIT_513 | Poutkak | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-28 16:00
IHS_EDA_063 | LIT_517 | Bihaing | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-28 14:00
IHS_DLA_124 | T0020 | Cite Bassa | Grid-Gen-Lithium | Indoor | GRATO | 1 | IPT TRION |  |  | 20 | [5 empty] | IPT 12 KW | DELTA |  | 5 | [6 empty] | RITAR 12V-180AH | RITAR 12V-180AH | 16 | [19 empty] | 2026-01-30 15:00
IHS_EDA_021 | T0136 | Dizangue | Grid-Gen | Indoor | GRATO | 1 | IPT TRION |  |  | 9 | [5 empty] | IPT 12KW | DELTA |  | 2 | [6 empty] | VISION 12V-170AH | VISION 12V-170AH | 16 | [15 empty] | BATTERY GE FAULTY/ FUITE D'HUILE AU BLOC MOTEUR |  |  |  | 2026-02-03 15:00
IHS_EDA_038 | T0137 | Mouanko Post Office | Grid-Gen | Indoor | GRATO | 1 | COLOR CERAMICA |  |  | 13 | [5 empty] | IPT - 12 KW | DELTA |  | 2 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 12 | [15 empty] | ;RCP FAULTY/ DISJONCTEUR INVERSEUR FAULTY/CONTACTEUR ENEO FAULTY; |  |  |  | 2026-01-27 10:00
IHS_EDA_035 | T0235 | Pouma Hospital | Grid-Gen | Indoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 2 | [6 empty] | MONBAT 12V/180AH | MONBAT 12V/180AH | 16 | [19 empty] | 2026-01-29 18:00
IHS_EDA_009 | T0262 | Ntoumba SDH | Grid-Gen-Lithium | Indoor | GRATO | 1 | TRION |  |  | 30 | [5 empty] | HUAWEI-36W | HUAWEI |  | 6 | [6 empty] | Lithium 100AH | Lithium 100AH | 6 | [19 empty] | 2026-02-04 10:09
IHS_DLA_125 | T0398 | Ndokoti | Grid-Gen | Indoor | GRATO | 1 | Tecno Gen |  |  | 15 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [19 empty] | 2026-01-30 07:00
IHS_DLA_253 | T0424 | Bonamoussadi2 | Grid-Gen | Outdoor | GRATO | 1 | MIKANO |  |  | 9 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | sacred sun 12V/175AH | sacred sun 12V/175AH | 16 | [19 empty] | 2026-01-28 14:00
IHS_EDA_001 | T0428 | Edea Town | Grid-Gen | Outdoor | GRATO | 1 | Olympian |  |  | 12.5 | [5 empty] | HUAWEI 12KW | HUAWEI |  | 2 | [6 empty] | MONBAT 12V-170AH | MONBAT 12V-170AH | 16 | [15 empty] | CARTE GE FAULTY |  |  |  | 2026-01-28 13:21
IHS_EDA_045 | T0491 | Sack Bayeme | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-29 12:00
IHS_DLA_171 | T0497 | Bassa Zone Industrielle | Grid-Gen | Indoor | GRATO | 1 | Tecno Gen |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 5 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [19 empty] | 2026-01-27 08:00
IHS_DLA_224 | T0499 | Denver | Grid-Gen | Outdoor | GRATO | 1 | MIKANO |  |  | 20 | [5 empty] | IPT - 12 KW | DELTA |  | 3 | [6 empty] | sacred sun 12V/175AH | sacred sun 12V/175AH | 16 | [19 empty] | 2026-02-04 09:30
IHS_DLA_139 | T0508 | Cite SIC | Grid-Gen | Outdoor | GRATO | 1 | Mikano |  |  | 9 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [19 empty] | 2026-01-26 11:00
IHS_BNB_034 | T0511 | Bonandalle | Grid-Gen | Outdoor | GRATO | 1 | Olympian |  |  | 12.5 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [15 empty] | ;PSC3 FAULTY/CLIM FAULTY /2 EXTRACTEURS FAULTY; |  |  |  | 2026-01-30 08:00
IHS_DLA_217 | T0522 | Makepe St Tropez | Grid-Gen | Outdoor | GRATO | 1 | Tecno Gen |  |  | 12.5 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 8 | [19 empty] | 2026-01-28 14:00
IHS_DLA_146 | T0598 | Total Ndokotti | Grid-Gen | Outdoor | GRATO | 1 | Earth technologies |  |  | 22 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 6 | [6 empty] | RITAR 12V/180AH | RITAR 12V/180AH | 16 | [19 empty] | 2026-01-27 14:00
IHS_DLA_230 | T0625 | Bonamoussadi3 | Grid-Gen | Outdoor | GRATO | 1 | IPT Power Tech Trion |  |  | 9 | [5 empty] | IPT 12KW | DELTA |  | 2 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 16 | [19 empty] | 2026-01-28 15:30
IHS_YND_538 | T0727 | Dibang | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-26 14:00
IHS_EDA_025 | T0762 | Sikom Mtn | Gen-Lithium | Indoor | GRATO | 2 | MIKANO |  |  | 20 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 6 | [6 empty] | Lithium 48V-100AH | Lithium 48V-100AH | 2 | [19 empty] | 2026-01-26 15:00
IHS_EDA_028 | T0770 | Ebombe2 | Gen Only | Indoor | GRATO | 2 | TRION |  |  | 20 | [5 empty] | IPT - 12 KW | DELTA |  | 3 | [6 empty] | Agisson 170 AH | Agisson 170 AH | 12 | [15 empty] | AFFICHEUR DE LA CARTE GE 2 FAULTY CAR IL A TOURNE MOINS DE 5H QUE PREVU/ COMPTEUR MECANIQUE A REMPLACE/ON A SUPPRIME LES COURANTS GE;CONTROLEUR PC3 FAULTY; |  |  |  | 2026-01-26 18:00
IHS_DLA_186 | T0865 | Bonamoussadi Sable | Grid-Gen | Outdoor | GRATO | 1 | Jubaili Bros |  |  | 17 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | Sacred sun 12V/175AH | Sacred sun 12V/175AH | 8 | [15 empty] | ;LE POWER CABINET IPT NE SE FERME PAS HERMETIQUEMENT SON SYSTÈME DE FERMETURE HS; |  |  |  | 2026-01-26 17:00
IHS_EDA_019 | T0575 | Ngoulmepa | Gen-Lithium | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 15 | [5 empty] | HUAWEI 24 KW | HUAWEI |  | 6 | [6 empty] | LITHIUM 48V-100AH | LITHIUM 48V-100AH | 3 | [19 empty] | 2026-01-26 13:00
IHS_BNB_013 | T0634 | Bonaminkano | Grid-Gen | Outdoor | GRATO | 1 | Tecno Gen |  |  | 20 | [5 empty] | ZTE 36KW | ZTE |  | 9 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 5 | [19 empty] | 2026-01-26 22:17
IHS_DLA_274 | T1128 | Kotto Village | Grid-Gen | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | SACRED SUN 12V/175AH | SACRED SUN 12V/175AH | 16 | [15 empty] | ;3 EXTRACTEURS FAULTY/ VENTILLATEUR EVAPORATEUR FAULTY; |  |  |  | 2026-02-11 08:00
IHS_BNB_027 | T1129 | Bonadale 2 | Grid-Gen | Outdoor | GRATO | 1 | Jubaili Bros |  |  | 17 | [5 empty] | IPT 12KW | DELTA |  | 2 | [6 empty] | SACRED SUN 12V-180AH | SACRED SUN 12V-180AH | 16 | [19 empty] | 2026-01-27 16:00
IHS_EDA_034 | T1139 | MBambu | Gen-Lithium | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 13 | [5 empty] | Huawei - 24 KW | HUAWEI |  | 6 | [6 empty] | Lithium 100AH | Lithium 100AH | 2 | [15 empty] | FUITE D'HULE AU NIVEAU DU CARTER;AUTONOMIE TRES FAILBLE; |  |  |  | 2026-01-27 19:00
IHS_DLA_482 | T1140 | MALIMBA | Hybrid-Gen | Outdoor | GRATO | 1 | IPT TRION |  |  | 15 | [5 empty] | IPT-12KW | DELTA |  | 2 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [15 empty] | ;BACKUP FAIBLE; |  |  |  | 2026-01-27 13:00
IHS_BNB_024 | T1700 | NKOMBA 2 | Grid-Gen | Outdoor | GRATO | 1 | Color ceramica |  |  | 20 | [5 empty] | HUAWEI 24 KW | HUAWEI |  | 6 | [6 empty] | VISION 48V/100AH | VISION 48V/100AH | 3 | [15 empty] | ;BACKUP NUL; |  |  |  | 2026-01-27 17:00
IHS_BNB_115 | T1163 | BONABERI 105 GABONAIS | Grid-Gen-Lithium | Outdoor | GRATO | 1 | ELCOS |  |  | 15 | [5 empty] | DPC 24KW | DPC |  | 3 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 3 | [19 empty] | 2026-01-29 18:00
IHS_EDA_041 | T0410 | Song Loulou | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | no name | no name | 16 | [19 empty] | 2026-02-07 07:00
IHS_DLA_206 | T0517 | Song Kot | Grid-Gen | Outdoor | GRATO | 1 | JUBALI BROSS |  |  | 30 | [5 empty] | Huawei - 24 KW | HUAWEI |  | 8 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 32 | [15 empty] | CABLE D'ALIMENTATION CHARGEUR STATIQUE PLUS ORDRE DE DEMARRAGE FAULTY |  |  |  | 2026-01-27 12:00
IHS_BNB_010 | T0112 | Sodiko | Grid-Gen | Indoor | GRATO | 1 | JMG |  |  | 30 | [5 empty] | ZTE 36 KW | ZTE |  | 9 | [6 empty] | VISION 53V/150AH | VISION 53V/150AH | 4 | [19 empty] | 2026-01-27 21:49
IHS_DLA_300 | T0720 | Mbongo | Grid-Gen | Outdoor | GRATO | 1 | IPT TRION |  |  | 15 | [5 empty] | IPT - 12 KW | DELTA |  | 3 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 3 | [15 empty] | RCP, RELAIS ENEO ET GE FAULTY |  |  |  | 2026-01-29 18:00
IHS_DLA_469 | T1187 | MABANDA 4 | Grid-Gen | Outdoor | GRATO | 1 | YOUNESS |  |  | 20 | [5 empty] | IPT 12 KW | DELTA |  | 4 | [6 empty] | MONBAT 12V 180 AH | MONBAT 12V 180 AH | 16 | [19 empty] | 2026-01-28 12:10
IHS_EDA_053 | T2742 | DIZANGUE KM14 | Grid-Gen | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 9 | [5 empty] | IPT 12 KW | DELTA |  | 2 | [6 empty] | SACRED SUN 12V-170AH | SACRED SUN 12V-170AH | 16 | [15 empty] | ;RELAIS GE, ENEO ET RCP FAULTY; |  |  |  | 2026-01-26 10:00
IHS_EDA_055 | T1654 | NDJOKLOUMBE | Hybrid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT - 12 KW | DELTA |  | 3 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 2 | [19 empty] | 2026-01-27 17:02
IHS_EDA_002 | T1285 | Logbele Edea | Grid-Gen | Outdoor | GRATO | 1 | SACCAL |  |  | 22 | [5 empty] | IPT - 12 KW | DELTA |  | 2 | [6 empty] | VISION 48v/150AH | VISION 48v/150AH | 3 | [15 empty] | MELANGE D'HUILE ET DU GASOIL DANS LE MOTEUR CAR LA POMPE A INJECTION EST FAULTY |  |  |  | 2026-01-28 08:14
IHS_EDA_046 | T0409 | Yo Yo | Gen-Lithium | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 20 | [5 empty] | IPT - 12 KW | DELTA |  | 6 | [6 empty] | LITHUIM 48V-100AH | LITHUIM 48V-100AH | 2 | [19 empty] | 2026-01-27 08:00
IHS_DLA_409 | T1932 | Mabanda 2 | Grid-Gen | Outdoor | GRATO | 1 | MIKANO |  |  | 30 | [5 empty] | IPT 12 KW | DELTA |  | 3 | [6 empty] | MONBAT 12V 180 AH | MONBAT 12V 180 AH | 16 | [19 empty] | 2026-01-26 20:30
IHS_DLA_480 | T3026 | BONASSAMA NEW | Grid-Gen-Lithium | Indoor | GRATO | 0 | IPT TRION |  |  | 30 | [5 empty] | HUAWEI 24KW | HUAWEI |  | 6 | [6 empty] | LITHUIM 48V-100AH | LITHUIM 48V-100AH | 4 | [19 empty] | 2026-01-27 13:22
IHS_EDA_033 | T0092 | Ngwei II | Solar-Gen | Indoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 3 | [6 empty] | MONBAT 12V-176AH | MONBAT 12V-176AH | 16 | [19 empty] | 2026-01-26 09:00
IHS_EDA_011 | T0087 | Edea peage | Grid-Gen | Indoor | GRATO | 1 | MIKANO |  |  | 13 | [5 empty] | IPT - 12 KW | DELTA |  | 3 | [6 empty] | RITAR 180AH | RITAR 180AH | 16 | [15 empty] | AFFICHEUR DE LA CARTE GE FAULTY / BATTERY GE FAULTY |  |  |  | 2026-02-02 11:00
IHS_DLA_252 | T1387 | Makepe2 | Grid-Gen | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 20 | [5 empty] | ZTE 36 KW | ZTE |  | 9 | [6 empty] | VISION 48V/150AH | VISION 48V/150AH | 4 | [19 empty] | 2026-01-26 15:00
IHS_DLA_297 | T0168 | Missole II PK 35 | Solar-Gen-Lithium | Outdoor | GRATO | 1 | IPT TRION |  |  | 20 | [5 empty] | Huawei - 24 KW | HUAWEI |  | 6 | [6 empty] | Lithium 48V/150AH | Lithium 48V/150AH | 4 | [19 empty] | 2026-01-26 17:00
IHS_BNB_116 | T1237 | BONAMINKANO MPANJO | Grid-Gen-Lithium | Outdoor | GRATO | 1 | MAHINDRA |  |  | 15 | [5 empty] | DPC 64KW | DPC |  | 4 | [6 empty] | 3 VISION 48V/100AH / 1 DPC 48V/100AH | 3 VISION 48V/100AH / 1 DPC 48V/100AH | 4 | [19 empty] | 2026-01-27 15:00
IHS_YND_593 | T1598 | Ngonga Water Tower | Grid-Gen | Outdoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 2 | [6 empty] | SACRED SUN 12V-175AH | SACRED SUN 12V-175AH | 16 | [19 empty] | 2026-02-02 16:00
IHS_DLA_155 | T1723 | Makepe Maturite | Grid-Gen | Outdoor | GRATO | 1 | IPT TRION |  |  | 12.5 | [5 empty] | IPT 24KW | DELTA |  | 3 | [6 empty] | SHL 12V/176AH | SHL 12V/176AH | 16 | [15 empty] | ;PSC3 FAULTY; |  |  |  | 2026-01-26 09:00
IHS_KRI_022 | T0176 | Mbongueng | Grid-Gen | Indoor | GRATO | 0 | TRION |  |  | 20 | [5 empty] | IPT - 12 KW | delta |  | 2 | [6 empty] | power cycle - 165 AH | power cycle - 165 AH | 16 | [19 empty] | 2026-01-26 15:10
IHS_KRI_013 | T0173 | Fifinda2 | Grid-Gen | Indoor | GRATO | 1 | TRION |  |  | 20 | [5 empty] | IPT 12KW | DELTA |  | 2 | [6 empty] | POWER CYCLE 12V-165AH | POWER CYCLE 12V-165AH | 16 | [15 empty] | ;PAS DE RCP/PSC3 FAULTY/TOUS LES FUSIBLE DE L'ATS FAULTY; |  |  |  | 2026-02-04 03:09
IHS_EDA_010 | T1847 | New Malimba | Grid-Gen | Outdoor | GRATO | 1 | JUBALIS BROS |  |  | 17 | [5 empty] | IPT - 12 KW | DELTA |  | 2 | [6 empty] | Monbat 170 AH | Monbat 170 AH | 16 | [15 empty] | ;1 SLOT DE REDRESSEUR FAULTY; |  |  |  | 2026-01-28 10:08
IHS_KRI_100 | T2015 | Elog Batindi/ Mombo Ville | Grid-Gen | Outdoor | GRATO | 1 | TECNO-GEN |  |  | 12.5 | [5 empty] | IPT - 12 KW | DELTA |  | 2 | [6 empty] | LITHIUM 48V/150AH | LITHIUM 48V/150AH | 2 | [15 empty] | CARTE GE FAULTY;CONTACTEUR GE ET PSC3 FAULTY; |  |  |  | 2026-01-26 14:32
IHS_DLA_501 | T2515 | MAKEPE ORCHIDEE | Grid-Gen-Lithium | Outdoor | GRATO | 1 | GB POWER |  |  | 15 | [5 empty] | FNS POWER 24 KW | FNS |  | 8 | [6 empty] | LITHUM 12V-100AH | LITHUM 12V-100AH | 1 | [15 empty] | ;2 RACK DE BATTERIE FONCTIONNELLE SUR 4; |  |  |  | 2026-01-28 09:00
IHS_DLA_505 | T2516 | Missoke Market | Gen-Lithium | Outdoor | GRATO | 1 | SACCAL |  |  | 15 | [5 empty] | FNS POWER 28.8KW | HUAWEI |  | 8 | [6 empty] | LITHUIM 48V-100AH | LITHUIM 48V-100AH | 1 | [19 empty] | 2026-01-26 06:00
IHS_DLA_512 | T3225 | TERMINUS BONAMOUSSADI | Grid-Gen-Lithium | Outdoor | GRATO | 1 | COLOR CERAMICA |  |  | 15 | [5 empty] | IPT 12KW | DELTA |  | 4 | [6 empty] | LITHUIM 48V-100AH | LITHUIM 48V-100AH | 4 | [19 empty] | 2026-01-30 17:00

## Sheet2
Rectifiers | [6 empty] | Generators |  |  |  |  | Batteries
## | Name on Rectifier | Rectifier Brand to keep | Rectifier Capaciy | Rectifier module | Module Capacity | Module Qty | ## | Name on GENERATOR | GENERATOR Brand to keep | Engine | Alternator | ## | Name on Batteries | Batteries Brand to keep | Type Batteries | Capacity | Commentaires | Statut
1 | Actura | Actura |  |  | 1.6 | 0 | 1 | Caterpillar | Caterpillar | Cat | Leroy somer | 1 | Agisson | Agisson | TCB-170AH | 170AH |  | OK | YES
2 | Chloride | Chloride | 10.8 | EVD1800 | 1.8 | 6 | 2 | CUMMINS | CUMMINS | Perkins | Stamford | 2 | CD TRUE | CD TRUE | FGC-176AH | 176AH |  | NOK | NO
3 | Delta O | Delta O | 9.6 | FR48-1600e | 1.6 | 6 | 3 | EART TECHNOLOGIE | EART TECHNOLOGIE | Perkins | Leroy somer | 3 | Dynamic power | DPC | 48-150AH | 150AH
4 | Delta I | Delta I | 16 | FR48-2000e | 2 | 8 | 4 | ELCOS 1 | ELCOS 1 | Perkins | Stamford | 4 | IPT | E2S | 48-100AH | 100AH
5 | DPC | DPC | 36 | SPIII48/4000HE | 4 | 9 | 5 | ELCOS 2 | ELCOS 2 | Perkins | Leroy somer | 5 | MONBATT | MONBATT | HVR-170AH | 170AH
6 | Eltek I | Eltek I | 10.8 | FP1800 | 1.8 | 6 | 6 | FG Wilson | FG Wilson | Perkins | Leroy somer | 6 | VESTWOODS / VT48150 | VESTWOODS | 48-150AH | 150AH
7 | Eltek O | Eltek O | 8 | FP2000 | 2 | 4 | 7 | Grenn Pool | Grenn Pool | Perkins | Leroy somer | 7 | RITAR | RITAR | FT-180AH | 180AH
8 | Emerson I | Emerson I | 9.6 | ESR-48/56 | 2.4 | 4 | 8 | HABIB 1 | HABIB | LISTER PETTER | Leroy somer | 8 | Vision / VLFP48150 | Vision | CGT-180AH | 180AH
9 | Emerson O | Emerson O | 10 | R48-2000e | 2 | 5 | 9 | HABIB 2 | HABIB | Perkins | Leroy somer | 9 | Sacred Sun | Sacred Sun | FTA-175AH / FHL-175AH | 175AH
10 | Ericsson | Ericsson | 10.8 | EFR48-56 | 2.7 | 4 | 10 | Trion | IPT Trion | Perkins | Leroy somer | 10 | POWER CYCLE | POWER CYCLE | PC-165AH | 165AH
11 | Huawei RBS | HW RBS | 4.5 | EPW30 | 1.5 | 3 | 11 | Jubaily Bros 1 | Jubaily Bros | LISTER PETTER | Leroy somer | 11 | HUAWEI | HUAWEI | EMS-100A3 | 100AH
12 | Huawei HB | HW HB | 9.6 | R4850N | 2.4 | 4 | 12 | Jubaily Bros 2 | Jubaily Bros | Perkins | Leroy somer | 12 | ZTE | ZTE | 48-150AH | 150AH
13 | Huawei WM | HW WM | 9.6 | EPW50 | 2.4 | 4 | 13 | LION ROCK | LION ROCK | Perkins | Leroy somer | 13 | SHOTO | SHOTO |  |  | Share the pictures
14 | Huawei 24 | HW24 | 24 | R4850G | 3 | 8 | 14 | LISTER PETER | LISTER PETER | KHOLER | Stamford | 14 | HOPPE | HOPPE |  |  | Share the pictures
15 | Huawei 30 | HW30 | 30 | R4850G2 | 3 | 10 | 15 | MEICO 2000 | MEICO 2000 | LISTER PETTER | Stamford | 15 | Gel battery | Gel battery |  |  | Share the pictures
16 | Huawei 36 | HW36 | 36 | R4875G | 4 | 9 | 16 | MIKANO 1 | MIKANO | Perkins | Leroy somer | 16 | DEEP CYCLE | DEEP CYCLE |  |  | Share the pictures
17 | IPT DC | Delta DC | 6.5 | NA | NA | NA | 17 | MIKANO 2 | MIKANO | Perkins | MECC ALTE |  | CD TRUE | CD TRUE | SHC-172AH | 172AH
18 | IPT Li | Delta Li | 27 | DPR3000B | 3 | 9 | 18 | MIKANO 3 | MIKANO | Perkins | Stamford |  | IPT | E2S | 48-150Ah | 150AH
19 | IPT Solar | Delta Solar | 20 | DPR4000B | 4 | 5 | 19 | MIKANO 4 | MIKANO | York | Leroy somer |  | MONBATT | MONBATT | MVR-180AH | 180AH
20 | IPT12 | Delta 12 | 12 | DPR2400B | 2.4 | 5 | 20 | POWERGEN | POWERGEN | Perkins | Leroy somer |  | HUAWEI | HUAWEI | 48-150AH | 150AH
21 | IPT24 | Delta 24 | 24 | DPR2400B | 2.4 | 10 | 21 | OLYMPIAN | OLYMPIAN | Perkins | Leroy somer |  | Energie storage System | E2S | 48-150Ah | 150AH
22 | Jerry Box | Jerry Box |  |  |  | #DIV/0! | 22 | POWERGEN | POWERGEN | Perkins | Leroy somer |  | Energie storage System | E2S | 48-100AH | 100AH
23 | Saft | Saft | 6.4 | SMR 44/34 | 1.6 | 4 | 23 | Pragmac | Pragmac | Perkins | Leroy somer |  | Vision / VLFP48150 | Vision | V-LFP-100 | 100AH
24 | FNS PWR28.8 | FNS PWR28.8 | 28.8 | MER048-50A | 2.4 | 12 | 24 | Color Cermica | Saccal Power Tech | Perkins | Leroy somer |  | Vision / VLFP48150 | Vision | 48-150AH | 150AH
25 | Vision SHW48 | Vision SHW48 | 42 | R4850G2 + S48-3KW | 3.0 / 3 | 6.0/8.0 | 25 | SDMO 1 | SDMO | KHOLER | Stamford
26 | ZTE | ZTE | 14.4 | ZXD2400 | 2.4 | 6 | 26 | SDMO 2 | SDMO | KHOLER | MECC ALTE
27 | ZTE36 | ZTE36 | 36 | R4875F1 | 4 | 9 | 27 | SDMO 3 | SDMO | Mitsubishi | MECC ALTE
28 | BC383 | BC383 |  |  |  | #DIV/0! | 28 | TECHNO GEN | TECHNO GEN | Perkins | Leroy somer
29 | Power One | Power One |  |  |  | #DIV/0! | 29 | YOUNES 1 | YOUNES | Perkins | Leroy somer
30 | PANASONIC | PANASONIC |  |  |  | #DIV/0! | 30 | YOUNES 1 | YOUNES | Perkins | Stamford
31 | MF1800/AHMER | MF1800/AHMER |  |  |  | #DIV/0! | 31 | Supernova | Supernova | Perkins | Leroy somer
32 | TENESOL | TENESOL |  |  |  | #DIV/0! | 32 | GB Power | GB Power | Perkins | Leroy somer
33 | Earth Technology | Earth Technology |  |  |  | #DIV/0! | 33 | Mahindra | Mahindra | Mahindra | Leroy somer
34 | AEG | AEG |  |  |  | #DIV/0! | 34 | Staunch Machinery 1 | Staunch Machinery | Perkins | Leroy somer
| Delta DC | Delta DC | 6.5 | NA | NA | NA | 35 | Staunch Machinery 2 | Staunch Machinery | Yanmar | Leroy somer
| Delta Li | Delta Li | 27 | DPR3000B | 3 | 9 |  | IPT PowerTech | IPT Trion | Perkins | Leroy somer
| Delta Solar | Delta Solar | 20 | DPR4000B | 4 | 5 |  | Jet Jenerator | Jubaily Bros | LISTER PETTER | Leroy somer
| Delta 12 | Delta 12 | 12 | DPR2400B | 2.4 | 5 |  | Jet Jenerator | Jubaily Bros | Perkins | Leroy somer
| Delta 24 | Delta 24 | 24 | DPR2400B | 2.4 | 10 |  | Color Ceramica | Staunch Machinery | Perkins | Leroy somer
[8 empty] | Color Ceramica | Staunch Machinery | Yanmar | Leroy somer
[8 empty] | Saccal Power Tech | Saccal Power Tech | Perkins | Leroy somer